## Sheet1
Test Conditions | Air Inlet Air Temps | Air Velocity | Ref Inlet Temp | Ref Inlet Pressure | Ref Flow Rate | Tested Ref Outlet Temp | Simulated Ref Outlet Temp | Approach Temp | Ref enthalpy difference | Tested pressure drop | Q_siml | Q_exp | Q | Ref out temp | pred T_approach | Q_new_FV | T_r_FV | predicted pressure drop
dim | C | m/s | C | MPa | kg/s | C | C | C | kJ/kg | kPa | kw | kw | kW | C | C | kw | C | kpa | 10seg | FV1 | 20 segms | FV2 | FV3 | 40 only plot | 80 only plot | FV4
1 | 29.4 | 1 | 118.1 | 9 | 0.038 | 40.4 | 38 | 10.7 | 186 |  | 8 | 7.1414 | 8.348 | 37.5981 | 8.1968 |  |  | 26.3627 | 7.55025272233 39.441596451 |  | 7.65689594964 39.2214357785 |  |  |  | 7.92284417596 38.6380599403
2 | 29.4 | 2 | 109.5 | 9 | 0.038 | 33.5 | 33.5 | 4.3 | 233.1 |  | 9 | 8.898 | 9.0047 | 32.9049 | 3.5036 |  |  | 23.1023 | 8.58580032583 35.0083298796 |  | 8.7008492603 34.4675195085 |  |  |  | 8.97245159767 33.0467297042
3 | 29.4 | 3 | 113.5 | 9 | 0.038 | 31.3 | 31.5 | 2.2 | 248.6 |  | 9.5 | 9.4733 | 9.4462 | 31.4733 | 2.0722 |  |  | 22.8967 | 9.25848305103 32.5800591778 |  | 9.34927069591 32.0397831188 |  |  |  | 9.53790602999 30.8467536893
4 | 29.4 | 1 | 124 | 10 | 0.038 | 41.5 | 36.9 | 12.2 | 214.8 |  | 9.25 | 8.2142 | 8.9217 | 38.1838 | 8.7822 |  |  | 22.5012 | 8.58632324421 39.8149351533 |  | 8.69354955079 39.3031026761 |  |  |  | 8.9616267275 37.9198783527
5 | 29.4 | 2 | 118 | 10 | 0.038 | 32.3 | 31.2 | 2.9 | 250.2 |  | 9.75 | 9.5268 | 9.4468 | 32.8892 | 3.4878 |  |  | 20.1771 | 9.42726093066 33.0022007563 |  | 9.50356988879 32.4452609068 |  |  |  | 9.66904422642 31.1944478491
6 | 29.4 | 3 | 117.1 | 10 | 0.038 | 31.1 | 30.3 | 1.6 | 253.1 |  | 9.9 | 9.637 | 9.592 | 31.4481 | 2.0468 |  |  | 19.6634 | 9.6270866798 31.1530513295 |  | 9.67620007878 30.770210991 |  |  |  | 9.77124141515 30.0154228305
7 | 29.4 | 1 | 128.8 | 11 | 0.038 | 40.4 | 34.3 | 11.2 | 234.3 |  | 9.9 | 8.9168 | 9.233 | 38.299 | 8.8972 |  |  | 19.8552 | 9.2320801765 38.271789745 |  | 9.32910202705 37.5904014705 |  |  |  | 9.56671206416 35.8436378621
8 | 29.4 | 2 | 123.5 | 11 | 0.038 | 31.7 | 30.4 | 2.4 | 257.8 |  | 10 | 9.8018 | 9.6932 | 32.6187 | 3.2171 |  |  | 18.0855 | 9.77835342893 31.8803780165 |  | 9.83192323814 31.4226370461 |  |  |  | 9.94257699617 30.461214975
9 | 29.4 | 3 | 123.1 | 11 | 0.038 | 30.9 | 29.9 | 1.4 | 259.4 |  | 10 | 9.873 | 9.8387 | 31.1979 | 1.7967 |  |  | 17.7543 | 9.90923487206 30.5652789852 |  | 9.94204729522 30.2768155689 |  |  |  | 10.0016539335 29.7482277229
10 | 35 | 1 | 121.3 | 9 | 0.038 | 43.1 | 40.6 | 7.8 | 163.1 |  | 7 | 6.2168 | 7.0496 | 40.9285 | 5.9274 |  |  | 28.1779 | 6.60153024218 41.8271604368 |  | 6.68723765651 41.6130029618 |  |  |  | 6.90135036975 41.1154286077
11 | 35 | 2 | 119.4 | 9 | 0.038 | 39.8 | 38.8 | 4.5 | 198.2 |  | 7.9 | 7.4979 | 8.3564 | 37.7659 | 2.7647 |  |  | 26.584 | 7.50554053523 39.6697406119 |  | 7.61861157369 39.4407507071 |  |  |  | 7.89656334132 38.851723153
12 | 35 | 3 | 118.8 | 9 | 0.038 | 38.2 | 37.9 | 3.1 | 214.3 |  | 8.1 | 8.1712 | 8.6641 | 36.6671 | 1.666 |  |  | 25.9726 | 7.97996734924 38.5894426593 |  | 8.09996373175 38.2982907615 |  |  |  | 8.38345845783 37.5224494704
13 | 35 | 1 | 127.7 | 10 | 0.038 | 45.5 | 41.9 | 10.4 | 191.8 |  | 8.2 | 7.2562 | 8.1476 | 42.4872 | 7.4857 |  |  | 24.3857 | 7.72830686391 43.8611706374 |  | 7.82673756017 43.533892135 |  |  |  | 8.07271712591 42.6830897388
14 | 35 | 2 | 122.6 | 10 | 0.038 | 38.7 | 37.9 | 3.6 | 230.3 |  | 8.8 | 8.7522 | 8.878 | 38.0316 | 3.0303 |  |  | 22.3135 | 8.60868112269 39.3696307725 |  | 8.70486651192 38.8934951762 |  |  |  | 8.92787274402 37.7143301173
15 | 35 | 3 | 122.2 | 10 | 0.038 | 37.2 | 36.6 | 2 | 236.9 |  | 9 | 9.0054 | 9.077 | 36.7801 | 1.779 |  |  | 21.8414 | 8.9464130511 37.4949803689 |  | 9.02087337721 37.0704059674 |  |  |  | 9.17665611072 36.1413423024
16 | 35 | 1 | 133.3 | 11 | 0.038 | 46 | 40.9 | 10.8 | 214.2 |  | 9 | 8.1321 | 8.7034 | 43.0572 | 8.0555 |  |  | 21.4873 | 8.55225764185 43.8265013114 |  | 8.64930194255 43.3049001906 |  |  |  | 8.89002993286 41.9463675022
17 | 35 | 2 | 128.9 | 11 | 0.038 | 38 | 36.6 | 2.9 | 244.2 |  | 9.5 | 9.281 | 9.2744 | 38.0466 | 3.0452 |  |  | 19.8004 | 9.2560722744 38.1435715751 |  | 9.32510345482 37.658256916 |  |  |  | 9.47477729388 36.5739514632
18 | 35 | 3 | 128.4 | 11 | 0.038 | 36.7 | 35.6 | 1.6 | 248.2 |  | 9.65 | 9.4351 | 9.4285 | 36.7485 | 1.7474 |  |  | 19.4383 | 9.44404219357 36.6067471315 |  | 9.49070221113 36.2602664981 |  |  |  | 9.58106163316 35.5775271409
19 | 29.4 | 1 | 94.8 | 9 | 0.076 | 41.1 | 41.1 | 11.7 | 111.7 |  | 10 | 11.1775 | 9.3407 | 43.6589 | 14.2573 |  |  | 92.2635 | 9.27691120005 43.1677335212 |  | 9.39445243362 42.9649869076 |  |  |  | 9.69608644189 42.4779394619
20 | 29.4 | 2 | 90.8 | 9 | 0.076 | 38.4 | 38.8 | 8.9 | 149.2 |  | 11.7 | 13.2194 | 12.9438 | 38.7385 | 9.3367 |  |  | 83.7435 | 11.489335589 39.8631279929 |  | 11.6708286289 39.6899345163 |  |  |  | 12.1324814081 39.2493365167
21 | 29.4 | 3 | 86.9 | 9 | 0.076 | 37.2 | 37.8 | 7.6 | 166.4 |  | 12.5 | 13.5942 | 14.2351 | 36.0377 | 6.6354 |  |  | 76.9744 | 12.6969291538 38.176469629 |  | 12.9117376596 37.9156128168 |  |  |  | 13.4548849551 37.1704344414
22 | 29.4 | 1 | 103.3 | 10 | 0.076 | 45.8 | 44.9 | 16.3 | 133.9 |  | 11.5 | 11.7356 | 11.0367 | 46.9798 | 17.5782 |  |  | 82.4691 | 10.9240491807 46.747977552 |  | 11.0582630407 46.5212025623 |  |  |  | 11.4022679839 45.9550376909
23 | 29.4 | 2 | 94.8 | 10 | 0.076 | 39.1 | 40.4 | 10 | 183.4 |  | 13.5 | 14.2827 | 14.0376 | 39.6998 | 10.2974 |  |  | 70.3293 | 13.2903407943 41.1307458549 |  | 13.4769324071 40.7505128377 |  |  |  | 13.954074744 39.7090478319
24 | 29.4 | 3 | 90.7 | 10 | 0.076 | 35.3 | 37.5 | 5.9 | 196.2 |  | 14.2 | 15.1043 | 14.8251 | 36.184 | 6.7813 |  |  | 64.4094 | 14.4218978277 37.2389811413 |  | 14.6096226756 36.7011834263 |  |  |  | 15.0772473087 35.2723072324
25 | 29.4 | 1 | 110.6 | 11 | 0.076 | 49.3 | 47 | 19.8 | 152.9 |  | 13 | 12.3406 | 12.3295 | 49.324 | 19.9221 |  |  | 74.3783 | 12.3095752552 49.0696119575 |  | 12.4551740022 48.761309704 |  |  |  | 12.8293510957 47.9630923385
26 | 29.4 | 2 | 100.7 | 11 | 0.076 | 38.4 | 39.5 | 8.8 | 198.8 |  | 14.8 | 15.2725 | 14.8324 | 39.8761 | 10.4732 |  |  | 62.1678 | 14.6634336926 40.2874802036 |  | 14.8429639427 39.7177850419 |  |  |  | 15.299344989 38.1987231718
27 | 29.4 | 3 | 97.1 | 11 | 0.076 | 33.9 | 35.6 | 4.7 | 209.4 |  | 15.7 | 16.0214 | 15.5129 | 35.8927 | 6.4896 |  |  | 57.6636 | 15.5440997934 35.6867292076 |  | 15.7018348757 35.0838009733 |  |  |  | 16.0836186331 33.5752128702
28 | 35 | 1 | 92.5 | 9 | 0.076 | 43.8 | 43.3 | 8.7 | 93 |  | 8 | 9.0039 | 7.7752 | 46.5162 | 11.5143 |  |  | 94.0044 | 7.89980308822 45.5452784624 |  | 7.99560550924 45.3110649743 |  |  |  | 8.24206738818 44.7387624367
29 | 35 | 2 | 90 | 9 | 0.076 | 40.2 | 40.9 | 5.1 | 117.8 |  | 9.5 | 11.4846 | 10.2019 | 41.5963 | 6.5946 |  |  | 87.7863 | 9.45256412157 42.0587485341 |  | 9.59220815392 41.8674205501 |  |  |  | 9.94918991799 41.4131730474
30 | 35 | 3 | 88.4 | 9 | 0.076 | 39.4 | 40 | 4.5 | 125.6 |  | 10 | 12.0721 | 11.6451 | 39.8444 | 4.8425 |  |  | 84.5168 | 10.2955608386 40.8044167495 |  | 10.4643703138 40.6281796822 |  |  |  | 10.8936118973 40.2007230965
31 | 35 | 1 | 104.1 | 10 | 0.076 | 48 | 47.2 | 12.8 | 118.6 |  | 10.2 | 10.5627 | 9.6744 | 49.8168 | 14.815 |  |  | 85.4463 | 9.75432492045 49.1520086052 |  | 9.87320249544 48.9012691294 |  |  |  | 10.1785350239 48.284631318
32 | 35 | 2 | 98.4 | 10 | 0.076 | 43.4 | 43.6 | 8.3 | 155.9 |  | 12 | 12.6258 | 12.5152 | 43.5894 | 8.5872 |  |  | 76.712 | 11.7034590181 44.5969133492 |  | 11.8725606605 44.3319145408 |  |  |  | 12.3044419577 43.647618112
33 | 35 | 3 | 93.9 | 10 | 0.076 | 41.1 | 42 | 6.1 | 168.9 |  | 12.5 | 13.3047 | 13.4315 | 40.8295 | 5.8272 |  |  | 71.3838 | 12.5837942674 42.2724701248 |  | 12.7695864381 41.9350617202 |  |  |  | 13.2384419913 41.029163796
34 | 35 | 1 | 109.6 | 11 | 0.076 | 51.5 | 49.7 | 16.4 | 134.9 |  | 11.5 | 11.2169 | 10.8672 | 52.2856 | 17.2838 |  |  | 76.5876 | 10.969912789 51.7034739702 |  | 11.0995872642 51.4187286022 |  |  |  | 11.4330156711 50.6972555805
35 | 35 | 2 | 101.9 | 11 | 0.076 | 43.6 | 44.3 | 8.6 | 177.5 |  | 13.5 | 13.7237 | 13.4398 | 44.3529 | 9.3504 |  |  | 66.6678 | 13.0654546091 45.1060175667 |  | 13.23569178 44.687847477 |  |  |  | 13.670116049 43.5755621716
36 | 35 | 3 | 98.4 | 11 | 0.076 | 40.5 | 41.6 | 5.2 | 186.6 |  | 14 | 14.3514 | 14.1935 | 40.9926 | 5.9899 |  |  | 62.3158 | 13.9563314557 41.5719613166 |  | 14.12252984 41.0777816792 |  |  |  | 14.5336588915 39.8002990098

## Sheet2
Test Conditions | Air Inlet Air Temps | Air Velocity | Refrigerant Inlet Temp | Refrigerant Inlet Pressure | Refrigerant Flow Rate | Tout
dim | C | m/s | C | MPa | kg/s | C
1 | 15 | 3 | 123.1 | 11 | 0.1
2 | 15 | 3 | 123.1 | 11 | 0.2