## definition
Condenser | definition
201 | 201 = user defined, 202 = circuited tube pattern, 203 = single finned tube,
0.0075 | tube inside diameter (m)
0.61 | tube length (m)
0.0002 | wall thickness of pipe (m), for micro-fin tubes, it doesn't include the fin height and the wall thickness
0.0287 | outside fin diameter (m)
0.0015 | fin pitch (m), fin space+one fin thickness
0.00013 | fin thickness (m)
0.024211 | spacing between tubes in bank (m) (P_t)
0.0125 | spacing between tubs in the longitudual direction (m) (P_l)
10 | number of segments per tube in finite difference model
0.0127 | radius of return bend (m)
-1 | nominal air mass flux (kg/s/m^2), correponding to the maximum air flux
1 | number of parallel branches in main section (circuit pattern model only)
54 | number of tubes in main branch (circuit pattern model only)
0 | number of tubes in subcooling branch (circuit pattern model only)
3 |  |  | number of banks
0.281 |  |  | Frontal area [m2]
1 |  |  | air side convection coefficient, for the first series test forTxV it is 1.0, since some unaccounted operation deviation
1 |  | refrigerant side two-phase flow convection coefficient
1 |  | refrigerant side subcooling convection coefficient
1 |  | refrigerant side pressure drop coefficient
1 |  | fouling factor (1.0-no, 0.0-completely)
0 |  |  | microfin type, 0=smooth tube, 1=helical, 2=cross-grooved, 3=herringbone
0 |  |  | fin number in a micro-fin tube
0 |  |  | fin apex angle in a micro-fin tube
0 |  |  | fin helix angle in a micro-fin tube
0 |  | fin height in a micro-fin tube
0 |  | base width of a single fin
0 |  |  | top width of a single fin
0 |  |  | base distance between two neighboring fins
5 |  |  | airside fin type, 1-plain, 2-corrugated, 3-slit, 4-louvered, 5-convex louvered, 6-smooth wavy, 7-spine
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
400 |  |  | tube wall conductance
237 |  |  | fin conductance