## definition
Evaporator | definition
301 | 301=user defined, 302 = circuited tube pattern, 303 = single finned tube
0.011735 | inside diameter of pipe (m), with respect to micro-fin tubes, this is the inside diameter at the fin tips
0.63182 | tube length (m)
0.0004826 | wall thickness of pipe (m), for micro-fin tubes, it doesn't include the fin height and the wall thickness
0.0127 | outside fin diameter (m)
0.0021167 | fin pitch (m), fin space+one fin thickness
0.0001905 | fin thickness (m)
0.03175 | spacing between tubes in bank (m)
0.027483 | spacing between tubs in the longitudual direction (m)
10 | number of segments per tube in finite difference model
0.015875 | radius of return bend (m)
2.55 | nominal air mass flux (kg/s/m^2), correponding to the maximum air flux
6 |  |  | Number of equivalent branches
12 |  |  | tube number in each evaporator branch
18 | number of rows high (tubes per bank)
4 | number of rows deep (numer of banks)
0.3623 |  | Frontal area
1 |  |  | air side convection coefficient (dry coil)
1 |  |  | refrigerant side convection coefficient
1 |  |  | refrigerant side pressure drop coefficient
1 |  |  | air side convection coefficient (wet coil);
1 | fouling factor (1.0-no, 0.0-completely)
0 |  |  | microfin type, 0=smooth tube, 1=helical, 2=cross-grooved, 3=herringbone
0 |  |  | fin number in a micro-fin tube
0 |  |  | fin apex angle in a micro-fin tube
0 |  |  | fin helix angle in a micro-fin tube
0 |  | fin height in a micro-fin tube
0 |  | base width of a single fin
0 |  |  | top width of a single fin
0 |  |  | base distance between two neighboring fins
6 |  |  | airside fin type, 1-plain, 2-corrugated, 3-slit, 4-louvered, 5-convex louvered, 6-smooth wavy, 7-spine
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
0 |  |  | substructure of fin surface
400 |  |  | tube wall conductance
237 |  |  | fin conductance